BUILDING MANAGEMENT SYSTEM PROPOSAL

CSIR Campus Building 53
Head Office Upgrade Project

Proposed BMS Architecture, HVAC Control Strategy & Implementation Approach

____

| PREPARED FOR CSIR | PREPARED BY Tshepo Mamabolo |
| --- | --- |
| COMPANY Spartcon | DATE 18 September 2026 |

Department of Science & Innovation, South Africa   ·   Basis of design derived from Building 53 HVAC mechanical drawings (issued for construction 07-05-2026).

Document Contents

CONTENTS   Table of Contents

01   Executive Summary & Project Understanding	3

02   Proposed BMS Solution	4

03   System Architecture	5

04   HVAC Control Strategy	6

05   Monitoring, Alarms, Trends & Scheduling	8

06   Communications & Network Architecture	9

07   Implementation & Commissioning	10

08   Assumptions, Exclusions & Information Required	11

09   Commercial Information & Sign-off	12

How to read this proposal. Technical statements are qualified against their level of certainty so that confirmed information is never presented as assumption, and engineering proposals are never presented as fact.

CONFIRMED   Established directly from the Building 53 HVAC drawings.     OEM   Supported by manufacturer capability, subject to model selection.     ENGINEERING   Proposed engineering basis of design.     CONFIRM   Requires client / OEM / HVAC contractor confirmation.

This proposal is based on the HVAC mechanical drawing set for Building 53. It does not constitute a complete BMS controls specification; the drawings do not define BMS network, controller I/O, sensor schedules or control sequences. Those items are addressed here as a proposed basis of design and are identified as requiring confirmation during detailed design.

Section 01

01   Executive Summary & Project Understanding

Spartcon has been asked to propose a Building Management System (BMS) for the CSIR Campus Building 53 – Head Office Upgrade Project. The proposed BMS will provide centralised monitoring and control of selected HVAC equipment through a network of field controllers and standard building-automation communication protocols, presented to operators through a web-based interface.

This proposal is developed from the HVAC mechanical drawing set for Building 53, comprising the Ground, First, Second and Third Floor HVAC plans, the Roof Plan HVAC, and associated plot/log information. That set was issued for construction on 07 May 2026.

What the drawings confirm

The drawings are primarily mechanical HVAC documents. They confirm the presence of the following HVAC infrastructure and equipment:

GMS ducting

VAV diffusers

Return air grilles

Ablution extract / disc valves

High-wall split air-conditioning units

Outdoor heat pump / air-conditioning units

Refrigerant piping

Condensate / drain arrangements and HVAC construction details

What the drawings do not define

The drawing set does not contain a complete BMS controls specification. There is no confirmed information for the BMS network (BACnet or Modbus), controller platform, controller I/O schedules, sensor schedule, control sequences, actuator communication protocols, lighting-control network, network topology, remote-access architecture or final BMS point count. These items are treated in this proposal as a proposed engineering basis of design and are clearly identified as requiring confirmation.

Basis of the proposal. The HVAC consultant/designer identified on the mechanical drawings is not the author of this BMS proposal and is not associated with Spartcon. This document is prepared by Spartcon as an independent BMS proposal.

Proposed direction

The proposed solution is based around a Vector Controls architecture, treated as its own controls ecosystem rather than a Tridium JACE / Niagara system. Field devices connect to Vector X2 field controllers over BACnet MS/TP or Modbus RTU, which connect over the building Ethernet network to a Vector management platform serving a web-based operator interface. Controller models, quantities and the final management platform are established from the approved I/O schedule during detailed design.

| Project parameter | Position in this proposal |
| --- | --- |
| Project | CSIR Campus Building 53 – Head Office Upgrade Project CONFIRMED |
| Source information | Building 53 HVAC mechanical drawings, issued for construction 07-05-2026 CONFIRMED |
| Controls ecosystem | Vector Controls (Vector X2 field controllers) ENGINEERING |
| Management platform | Vector BAS-SMP-2000 as proposed basis; GSM-1000-BMX noted as alternative CONFIRM |
| BMS point count / I/O | To be established from the approved equipment schedule CONFIRM |

Section 02

02   Proposed BMS Solution

The proposed BMS is a Vector-based control architecture. Field devices and HVAC equipment interfaces are connected to Vector X2 field controllers, which communicate over standard building-automation buses to a Vector management platform. Operators interact with the system through a browser-based interface for monitoring, alarms, trends and scheduling.

Vector X2 field controllers

Vector X2 controllers are presented as programmable communicating field controllers within the Vector controls ecosystem. Depending on the controller model selected, relevant communication capabilities include:

BACnet MS/TP

BACnet/IP

Modbus RTU / ASCII

Modbus TCP

Controller configuration and programming are associated with the Vector EasySet environment. Controller model selection and quantities are not fixed in this proposal; they will be determined from the final I/O schedule and the equipment interfaces confirmed during detailed design.

Management platform

The proposed basis of design for the management layer is the Vector BAS-SMP-2000. A second Vector management product, GSM-1000-BMX, is noted as a possible alternative subject to final system selection. No single management platform is treated as finally selected; the platform above is stated as the proposed basis only.

Vector compared with a Tridium JACE / Niagara system

This distinction is important and is stated precisely:

| Tridium JACE / Niagara | Vector Controls |
| --- | --- |
| A JACE is a hardware/network automation controller that runs the Niagara framework. | Vector X2 controllers are independent field controllers belonging to the Vector controls ecosystem. |
| Niagara Workbench is used to engineer and configure Niagara systems. | Vector has its own configuration environment (Vector EasySet). Vector is not used to program a JACE. |
| Communicates using standard protocols including BACnet and Modbus. | Communicates using standard protocols including BACnet and Modbus, and can therefore operate as an independent BMS/control architecture. |

Because both platforms use standard communication protocols, a Vector + Niagara/JACE hybrid architecture is technically possible where appropriate. However, this proposal is primarily evaluating a Vector-based architecture. No official partnership between Vector and Tridium is implied or claimed.

Scope note. The described capabilities reflect the Vector product ecosystem. Final controller models, the management platform, and the exact protocol used per equipment item remain subject to confirmation during detailed design and against the approved equipment schedule.

Section 03

03   System Architecture

The proposed architecture is a conventional layered building-automation topology: field devices report to field controllers, field controllers communicate over field buses to the management layer, and the management layer presents a web-based interface. The diagram below shows the proposed conceptual architecture.

Diagram is conceptual. The final physical network architecture, device addressing and protocol assignment per equipment item are coordinated with the client IT/network team and confirmed against the approved equipment schedule during detailed design.

Section 04

04   HVAC Control Strategy

The following proposed control strategy describes the intended BMS functions per equipment type. In every case the final control points depend on the selected equipment, its controller/actuator and its available communication interface, and are confirmed during detailed design.

VAV systems

Where the installed VAV equipment supports suitable control interfaces, the BMS should be capable of:

Monitoring zone temperature

Monitoring relevant zone conditions

Adjusting temperature/setpoint parameters where supported

Monitoring VAV operating status

Monitoring airflow-related values where available

Managing occupied/unoccupied operation where applicable

Generating alarms for abnormal conditions

Trending relevant values

No particular actuator or communication protocol is assumed for any VAV. Final control points depend on the selected VAV controller/actuator.  CONFIRM

Temperature / humidity / CO₂

The proposed system supports environmental sensors for temperature, relative humidity and CO₂. Where required by the final design, these values can be used for monitoring, alarming, trending and setpoint/control strategies. Exact sensor quantities and acceptable limits are not defined at this stage.  CONFIRM

Heat pump / air-conditioning systems

The drawings identify outdoor heat pump / AC equipment with the following ratings taken from the mechanical drawings:

| Equipment | Rating (from drawings) | Status |
| --- | --- | --- |
| HP/AC01 | 302.1 kW | CONFIRMED |
| HP/AC02 | 585.8 kW | CONFIRMED |

Manufacturer, model, protocol and exact control interface are not defined by the drawings. BMS integration will depend on the equipment OEM interface and may use BACnet, Modbus, dry contacts, gateway integration or another approved interface as applicable. Potential monitoring/control functions — all subject to OEM confirmation — may include enable/disable where supported, run status, fault/alarm status, operating mode, temperature values, setpoints and relevant equipment parameters.  OEM

Section 04 · continued

04   HVAC Control Strategy (continued)

Split air-conditioning units

The drawings include high-wall split units. Integration depends on the selected split-unit manufacturer's available communication interface. Possible approaches include:

Direct BACnet / Modbus interface

Manufacturer gateway

Approved third-party interface

Monitoring-only integration where full control is unavailable

Direct integration is not claimed without confirmation of the selected manufacturer's interface.  OEM

Extract systems

The proposal addresses monitoring/control of relevant extract systems where applicable. Potential points include:

Run status

Fault status

Enable/disable

Scheduling

Final points depend on the installed equipment.  CONFIRM

Summary of proposed points by equipment type

| Equipment | Typical proposed functions | Dependency |
| --- | --- | --- |
| VAV zones | Zone temperature, zone conditions, setpoint adjust (where supported), status, airflow (where available), occupancy mode, alarms, trends | Selected VAV controller/actuator |
| Environmental sensors | Temperature, RH, CO₂ — monitoring, alarming, trending, control strategies | Final design / sensor selection |
| Heat pump / AC (HP/AC01, HP/AC02) | Enable/disable, run status, fault, mode, temperatures, setpoints, parameters | OEM interface |
| Split AC units | Monitoring and control per available interface; monitoring-only where control unavailable | Manufacturer interface / gateway |
| Extract systems | Run status, fault, enable/disable, scheduling | Installed equipment |

Point allocation. The functions above are a proposed control strategy. Final point allocation will be established from the approved equipment schedule and confirmed control philosophy during detailed design.

Section 05

05   Monitoring, Alarms, Trends & Scheduling

Graphics

A browser-based graphical interface is provided for building overview, floor-level views, HVAC equipment, VAV zones, environmental conditions, equipment status and alarms. Graphics reflect the equipment confirmed in the drawings and the points established during detailed design.

Alarms

Centralised alarms are provided for conditions such as equipment faults, communication failures, sensor faults, abnormal operating conditions and other relevant HVAC alarms. Alarm points and thresholds are confirmed against the final control philosophy.

Trends

Historical trending is provided for relevant temperature, humidity, CO₂, equipment status, setpoints and other selected BMS points.

Scheduling

Schedules may be used for occupied/unoccupied operation, HVAC enable/disable, equipment operating periods and other approved schedules.

Data / reporting

Where supported by the selected management platform, the system provides historical data, alarm history, trends, operating information and basic reporting. Advanced analytics are not promised and are only included where specifically supported by the selected platform and agreed in scope.

| Function | Description | Basis |
| --- | --- | --- |
| Graphics | Building overview, floor views, HVAC equipment, VAV zones, conditions, status, alarms | ENGINEERING |
| Alarms | Equipment faults, comms failures, sensor faults, abnormal conditions, HVAC alarms | ENGINEERING |
| Trends | Temperature, humidity, CO₂, status, setpoints, selected points | ENGINEERING |
| Scheduling | Occupied/unoccupied, HVAC enable/disable, operating periods | ENGINEERING |
| Data / reporting | Historical data, alarm history, trends, operating info, basic reporting | CONFIRM |

Section 06

06   Communications & Network Architecture

Field controllers communicate with field devices over RS-485 field buses using BACnet MS/TP or Modbus RTU. The field controllers connect to the building Ethernet network, over which they communicate with the Vector management server using BACnet/IP or Modbus TCP. The management server presents the web-based operator interface.

The final physical network architecture must be coordinated with the client's IT/network team. The following considerations apply and are confirmed during detailed design:

| Consideration | Approach |
| --- | --- |
| IP addressing | Allocated in coordination with client IT. No IP addresses are assigned in this proposal. |
| Network segmentation / VLANs | Applied where required, coordinated with client IT policy. |
| Switch infrastructure | Confirmed against available building network infrastructure and BMS requirements. |
| RS-485 field buses | Field bus layout, termination and biasing per device count and cable runs. |
| Device addressing | BACnet/Modbus device addressing scheme defined in the I/O schedule. |
| Network commissioning | Bus and IP communication verified during commissioning. |
| Cybersecurity | Aligned with client requirements. Controllers are not exposed directly to the public internet. |
| Remote access | Provided only through an approved, secured method per client requirements. |

Security position. Controllers will not be exposed directly to the public internet. Remote access, segmentation and cybersecurity measures are implemented per the client's IT and security requirements, which are to be confirmed.

Existing building network availability, IT/VLAN requirements, remote-access requirements and client cybersecurity requirements are all subject to confirmation.  CONFIRM

Section 07

07   Implementation & Commissioning

Implementation follows a staged methodology. Each stage produces defined outputs that feed the next, so that hardware and programming decisions are grounded in a confirmed I/O schedule and control philosophy rather than assumptions.

| Stage | Activity | Scope |
| --- | --- | --- |
| 1 | Detailed design | Review final HVAC equipment schedule; confirm equipment manufacturers/models; confirm communication interfaces; develop I/O schedule; confirm network requirements; confirm control philosophy. |
| 2 | Hardware / panel preparation | Controller selection; sensor selection; actuator/interface selection; panel and network requirements. |
| 3 | Installation | Field controllers; sensors; communication cabling; network connections; equipment interfaces. |
| 4 | Programming | Controller configuration; control sequences; alarms; scheduling; graphics; trends. |
| 5 | Commissioning | Point-to-point testing; sensor verification; equipment command verification; alarm testing; communication testing; functional testing. |
| 6 | Handover | As-built information; controller/database backup; configuration documentation; operator orientation/training; final commissioning records. |

Dependency. Stage 1 outputs — the approved equipment schedule, confirmed interfaces, I/O schedule and control philosophy — determine controller models, quantities, sensor counts and final point allocation. These are not fixed in this proposal.

Programme durations, resourcing and sequencing are confirmed on award and against the project construction programme.

Section 08

08   Assumptions, Exclusions & Information Required

This proposal is a basis of design developed from HVAC mechanical drawings. The following items are not confirmed by the drawings and require confirmation before detailed implementation. No prices, equipment quantities, compliance requirements or client standards are fabricated in this document.

Requires confirmation

Final BMS point count

Exact Vector controller models

Exact controller quantities

Sensor quantities

VAV controller/actuator interfaces

HVAC OEM communication protocols

Split-unit integration

Heat pump / AC integration

Existing building network availability

IT / VLAN requirements

Remote access requirements

Lighting-control requirements

Client cybersecurity requirements

Final BMS server / management platform selection

Electrical power requirements

BMS panel requirements & final control sequences

Assumptions

The HVAC equipment identified in the Building 53 drawings represents the equipment to be integrated, subject to the final approved equipment schedule.

Selected HVAC equipment provides accessible communication interfaces or points suitable for BMS integration; interface type is confirmed per OEM.

A suitable building network is made available, or its requirements are agreed with client IT.

Exclusions

Mechanical HVAC supply, installation and associated works.

OEM equipment, gateways or licences not confirmed in the agreed BMS scope.

Building IT network infrastructure beyond the BMS interface, unless specifically agreed.

Electrical power provision to BMS panels and equipment, unless specifically agreed.

Lighting-control scope, unless specifically agreed and defined.

Information required from client / consultant / HVAC contractor

Approved HVAC equipment schedule with manufacturers and models; OEM communication interface details for heat pump/AC, split units and extract systems; VAV controller/actuator details; building network and IT/security requirements; remote-access requirements; and confirmation of any lighting-control scope.

Section 09

09   Commercial Information & Sign-off

PRELIMINARY — TO BE COMPLETED

The table below is a preliminary commercial structure to be completed once the equipment schedule, I/O schedule and control philosophy are confirmed. No prices, quantities, labour rates or costs are stated at this stage.

| Item | Description | Qty | Unit Rate | Amount |
| --- | --- | --- | --- | --- |
| BMS controllers | To be confirmed | TBC | TBC | TBC |
| Sensors | To be confirmed | TBC | TBC | TBC |
| BMS management system | Proposed Vector platform | TBC | TBC | TBC |
| Installation | Field installation | TBC | TBC | TBC |
| Programming & commissioning | BMS configuration and commissioning | TBC | TBC | TBC |

This table is a placeholder for commercial information to be completed later. It does not represent a quotation.

Conclusion

This proposal sets out a Vector-based BMS approach for CSIR Campus Building 53, developed from the available HVAC mechanical drawings. It describes the proposed architecture, HVAC control strategy, BMS functions, network approach and staged implementation, while clearly separating what is confirmed by the drawings from what remains a proposed engineering basis of design. The information identified as requiring confirmation should be resolved with the client, OEMs and HVAC contractor during detailed design, after which controller models, quantities, point counts and commercial values can be finalised.

Acceptance & Sign-off

| FOR AND ON BEHALF OF SPARTCON Name Signature Date | FOR AND ON BEHALF OF CSIR Name Signature Date |
| --- | --- |

Prepared by Tshepo Mamabolo, Spartcon · Prepared for CSIR · 18 September 2026 · CSIR Campus Building 53 – Head Office Upgrade Project.